Copyright 2010 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 09 65 19 - RESILIENT TILE FLOORING

GENERAL

RELATED DOCUMENTS

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

The Contractor's attention is specifically directed, but not limited, to the following documents for additional requirements:

Uniform General Conditions for Construction Contracts, State of Texas, 2010(UGC).

The University of Houston’s Supplemental General Conditions and Special Conditions for Construction.

SUMMARY

Section Includes:

Solid vinyl floor tile.

Rubber floor tile.

Vinyl composition floor tile.

Related Sections:

Section 09 65 13 "Resilient Base and Accessories" for resilient base, reducer strips, and other accessories installed with resilient floor coverings.

Section 09 65 16 "Resilient Sheet Flooring" for resilient sheet floor coverings.

ACTION SUBMITTALS

Product Data:  For each type of product indicated.

Shop Drawings:  For each type of floor tile.  Include floor tile layouts, edges, columns, doorways, enclosing partitions, built-in furniture, cabinets, and cutouts.

Show details of special patterns.

Samples for Verification:  Full-size units of each color and pattern of floor tile required.

Seam Samples:  For seamless-installation technique indicated and for each flooring product, color, and pattern required; with seam running lengthwise and in center of 6-by-9-inch (150-by-230-mm)  Sample applied to a rigid backing and prepared by Installer for this Project.

Product Schedule:  For floor tile.  Use same designations indicated on Drawings.

INFORMATIONAL SUBMITTALS

Qualification Data:  For qualified Installer.

CLOSEOUT SUBMITTALS

Maintenance Data:  For each type of floor tile to include in maintenance manuals.

MATERIALS MAINTENANCE SUBMITTALS

Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

Floor Tile:  Furnish 1 box for every 50  boxes or fraction thereof, of each type, color, and pattern of floor tile installed.

QUALITY ASSURANCE

Installer Qualifications:  A qualified installer who employs workers for this Project who are competent in techniques required by manufacturer for floor tile installation and seaming method indicated.

Engage an installer who employs workers for this Project who are trained or certified by manufacturer for installation techniques required.

Fire-Test-Response Characteristics:  As determined by testing identical products according to ASTM E 648 or NFPA 253 by a qualified testing agency.

Critical Radiant Flux Classification:  Class I, not less than 0.45 W/sq. cm.

DELIVERY, STORAGE, AND HANDLING

Store floor tile and installation materials in dry spaces protected from the weather, with ambient temperatures maintained within range recommended by manufacturer, but not less than 50 deg F (10 deg C) or more than 90 deg F (32 deg C).  Store floor tiles on flat surfaces.

PROJECT CONDITIONS

Maintain ambient temperatures within range recommended by manufacturer, but not less than 70 deg F (21 deg C)  or more than 95 deg F (35 deg C) , in spaces to receive floor tile during the following time periods:

48 hours before installation.

During installation.

48 hours after installation.

Until Substantial Completion, maintain ambient temperatures within range recommended by manufacturer, but not less than 55 deg F (13 deg C)  or more than 95 deg F (35 deg C) .

Close spaces to traffic during floor tile installation.

Close spaces to traffic for 48 hours after floor tile installation.

Install floor tile after other finishing operations, including painting, have been completed.

PRODUCTS

PERFORMANCE REQUIREMENTS

SOLID VINYL FLOOR TILE

Products:  Subject to compliance with requirements,  provide one of the following :

Amtico, Mannington Commerical.; <Insert product name or designation>.

Armstrong World Industries, Inc.; Vinyl Tile.

Tarkett, Inc.; Aria.

Substitutions:  see Section 01 25 00 – Substitution Procedures.

Tile Standard:  ASTM F 1700.

Class:   Class I, monolithic vinyl tile  .

Type:  Type A, smooth surface .

Thickness:     0.125 inch (3.2 mm) .

Size:  12 by 12 inches (305 by 305 mm)     .

Retain paragraph below if colors and patterns are not indicated in a separate schedule.

Colors and Patterns:    [As selected by Architect from full range of industry colors].

RUBBER FLOOR TILE

Products:  Subject to compliance with requirements,  provide one of the following :

Burke Mercer Flooring Products, Division of Burke Industries Inc.; Flecksible.

Flexco; Spextones.

Johnsonite; Cityscape Speckled Rubber Tile.

Substitutions:  see Section 01 25 00 – Substitution Procedures.

Tile Standard:  ASTM F 1344, Class I-A, homogeneous rubber tile, solid color   .

Hardness:  Not less than 85 as required by ASTM F 1344, measured using Shore, Type A durometer per ASTM D 2240 .

Wearing Surface:    Molded pattern.

Molded-Pattern Figure:  Raised discs  .

Thickness:  0.125 inch (3.2 mm) .

Size:  12 by 12 inches (305 by 305 mm)  .

VINYL COMPOSITION FLOOR TILE

Products:  Subject to compliance with requirements,  provide one of the following :

Armstrong World Industries, Inc.; Excelon.

Mannington Mills, Inc.; Essentials.

Tarkett, Inc.; .

Substitutions:  see Section 01 25 00 – Substitution Procedures.

Tile Standard:  ASTM F 1066, Homogenous, with color extending throughout thickness  .

Wearing Surface:  Smooth .

Thickness:  0.125 inch (3.2 mm) .

Size:  12 by 12 inches (305 by 305 mm).

Retain paragraph below if colors and patterns are not indicated in a separate schedule.

Colors and Patterns:    [As selected by Architect from full range of industry colors].

INSTALLATION MATERIALS

Trowelable Leveling and Patching Compounds:  Latex-modified, portland cement based or blended hydraulic-cement-based formulation provided or approved by manufacturer for applications indicated.

Adhesives:  Water-resistant type recommended by manufacturer to suit floor tile and substrate conditions indicated.

Adhesives shall comply with the following limits for VOC content when calculated according to 40 CFR 59, Subpart D (EPA Method 24):

VCT and Asphalt Tile Adhesives:  Not more than 50 g/L.

Rubber Floor Adhesives:  Not more than 60 g/L.

Floor Polish:  Provide protective liquid floor polish products as recommended by manufacturer.

EXECUTION

EXAMINATION

Examine substrates, with Installer present, for compliance with requirements for maximum moisture content and other conditions affecting performance of the Work.

Verify that finishes of substrates comply with tolerances and other requirements specified in other Sections and that substrates are free of cracks, ridges, depressions, scale, and foreign deposits that might interfere with adhesion of floor tile.

Proceed with installation only after unsatisfactory conditions have been corrected.

PREPARATION

Prepare substrates according to manufacturer's written instructions to ensure adhesion of resilient products.

Concrete Substrates:  Prepare according to ASTM F 710.

Verify that substrates are dry and free of curing compounds, sealers, and hardeners.

Remove substrate coatings and other substances that are incompatible with adhesives and that contain soap, wax, oil, or silicone, using mechanical methods recommended by manufacturer.  Do not use solvents.

Alkalinity and Adhesion Testing:  Perform tests recommended by manufacturer.  Proceed with installation only after substrates pass testing.

Moisture Testing:  Perform tests recommended by manufacturer and as follows.  Proceed with installation only after substrates pass testing.

Perform anhydrous calcium chloride test, ASTM F 1869.  Proceed with installation only after substrates have maximum moisture-vapor-emission rate of 3 lb of water/1000 sq. ft. (1.36 kg of water/92.9 sq. m)  in 24 hours.

Perform relative humidity test using in situ probes, ASTM F 2170.  Proceed with installation only after substrates have a maximum 75%  relative humidity level measurement.

Access Flooring Panels:  Remove protective film of oil or other coating using method recommended by access flooring manufacturer.

Fill cracks, holes, and depressions in substrates with trowelable leveling and patching compound and remove bumps and ridges to produce a uniform and smooth substrate.

Do not install floor tiles until they are same temperature as space where they are to be installed.

Move resilient products and installation materials into spaces where they will be installed at least 48 hours in advance of installation.

Sweep and vacuum clean substrates to be covered by resilient products immediately before installation.

FLOOR TILE INSTALLATION

Comply with manufacturer's written instructions for installing floor tile.

Lay out floor tiles from center marks established with principal walls, discounting minor offsets, so tiles at opposite edges of room are of equal width.  Adjust as necessary to avoid using cut widths that equal less than one-half tile at perimeter.

Lay tiles square with room axis  in pattern indicated .

Match floor tiles for color and pattern by selecting tiles from cartons in the same sequence as manufactured and packaged, if so numbered.  Discard broken, cracked, chipped, or deformed tiles.

Lay tiles   in pattern of colors and sizes indicated.

Scribe, cut, and fit floor tiles to butt neatly and tightly to vertical surfaces and permanent fixtures including built-in furniture, cabinets, pipes, outlets, and door frames.

Extend floor tiles into toe spaces, door reveals, closets, and similar openings.  Extend floor tiles to center of door openings.

Maintain reference markers, holes, and openings that are in place or marked for future cutting by repeating on floor tiles as marked on substrates.  Use chalk or other nonpermanent, nonstaining marking device.

Install floor tiles on covers for telephone and electrical ducts, building expansion-joint covers, and similar items in finished floor areas.  Maintain overall continuity of color and pattern between pieces of tile installed on covers and adjoining tiles.  Tightly adhere tile edges to substrates that abut covers and to cover perimeters.

Adhere floor tiles to flooring substrates using a full spread of adhesive applied to substrate to produce a completed installation without open cracks, voids, raising and puckering at joints, telegraphing of adhesive spreader marks, and other surface imperfections.

CLEANING AND PROTECTION

Comply with manufacturer's written instructions for cleaning and protection of floor tile.

Perform the following operations immediately after completing floor tile installation:

Remove adhesive and other blemishes from exposed surfaces.

Sweep and vacuum surfaces thoroughly.

Damp-mop surfaces to remove marks and soil.

Protect floor tile products from mars, marks, indentations, and other damage from construction operations and placement of equipment and fixtures during remainder of construction period.

Floor Polish:  Remove soil, visible adhesive, and surface blemishes from floor tile surfaces before applying liquid floor polish.

Apply  two   coat(s).

Cover floor tile until Substantial Completion.

END OF SECTION 09 65 19