SECTION 27 0543 – UNDERGROUND DUCT AND RACEWAYS

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect" or “Engineer.” Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

Delete hidden text after this Section has been edited for the Project.

1. GENERAL
   * + 1. RELATED DOCUMENTS
          1. The Contractor's attention is specifically directed, but not limited, to the following documents for additional requirements:

The current version of the *Uniform General Conditions for Construction Contracts*, State of Texas available on the web site of the Texas Facilities Commission.

The University of Houston’s *Supplemental General Conditions and Special Conditions for Construction*.

The University of Houston’s *Network Infrastructure Design Standards* (available at <https://uh.edu/infotech/services/computing/networks/network-infra-standards/>).

* + - 1. SUMMARY
         1. Section Includes:

Revise subparagraph(s) below to suit Project.

Cutting and Patching Asphalt and Concrete.

Trenching and Excavation

Underground Conduit Systems.

Cable Routing Hardware.

Horizontal Directional Drilling – Also commonly referred to as Directional Boring or Guided Horizontal Boring.

* + - * 1. Work covered by this Section consists of providing all services, labor, materials, tools, and equipment required for the complete and proper installation of exterior telecommunications pathways as called for in these Specifications and related Drawings.
        2. Detailed summary of work *(Designer to provide a detailed summary of all work to be performed.)*

Incoming Service Duct-bank: [**Description**]

Primary Duct-bank: [**Description**]

Feeder Duct-bank: [**Description**]

Innerduct: [**Description**]

* + - 1. PREINSTALLATION MEETINGS
         1. Preconstruction Conference: Conduct conference at [**Project site**] <**Insert location**>. The Contractor and the Facilities Project Manager lead the meeting. The UIT Project Manager must be invited to the Preinstallation meetings.

Copy subparagraph below and edit for each activity required for preconstruction conference.

<Insert activity>.

* + - 1. SUBMITTAL ADMINISTRATIVE REQUIREMENTS
         1. Follow the *Submittal Administrative Requirements* as statedin *Section 01 3300 Submittal Procedures*. For submittals to UIT, use electronic format only.
      2. ACTION SUBMITTALS
         1. Before installation begins:

Provide notification, in writing, of conditions detrimental to proper completion of the Work or conditions deviating from Drawings.

Provide Shop Drawings of all core drilling locations for coordination with Architect and Owner prior to drilling.

Obtain University Information Technology Network Services (UITNS) approval before installation proceeds.

* + - 1. INFORMATIONAL SUBMITTALS
         1. AS-BUILT DRAWINGS

Submit drawings with notations reflecting any variations from the Specifications and Drawings, including As-built conduit routing.

Provide Excel spreadsheet with GPS coordinates of all handholds and manholes.

* + - 1. QUALITY ASSURANCE
         1. Perform all installation work for the new exterior telecommunications pathways in a neat and workmanlike manner.
         2. Materials and work specified herein shall comply with the applicable requirements as stated in *Section 27 0500 Communications General Provisions.*
         3. For horizontal directional drilling, the Contractor shall follow all procedural precautions necessary to ensure that the essential aspects of proper directional bore installation are adequately controlled.

1. PRODUCTS

The paragraph and subparagraphs in this Article demonstrate the line spacing format for subparagraphs not subordinate to the preceding subparagraph.

* + - 1. PARTS AND MANUFACTURERS
         1. Refer to *Section 01 2500 Substitution Procedures* for variations from approved manufacturers or parts. **Obtain written approval from UITNS before requesting a substitution for work covered by *Division 27 Communications.***
         2. TRENCH/BACKFILL MATERIALS

Refer to *Division 31 Trenching, Backfilling, and Compaction* for requirements.

* + - * 1. CONDUIT SYSTEM

Non-Metallic Conduit:

PVC plastic pipe: ASTM D1785, Schedule 40, Type PVC 1120.

Tone Tape: Arnco DL WP12LC Tone Tape, or equivalent.

Electrical Metallic Tubing (EMT): Electro-galvanized steel tubing ¾ inch and larger diameter per project requirements.

Conduit joint couplings and connectors - steel double set screw indenter fittings.

Metal bushings for ¾-inch and 1-inch conduit.

Insulated metallic bushings for 1-1/4 inch and larger conduit.

Insulated metallic bushings with grounding lugs as required.

Conduit sweeps - minimum 10 times the conduit inside diameter.

Include required conduit straps and hangers, heavy-duty malleable iron or steel. Perforated pipe strap and wire hangers are not permitted.

Inside Pull-Boxes: Refer to *Section 27 0528 Pathways for Communications Systems* for inside pull-boxes for conduit entering building.

Outside Pull-Boxes: Minimum 14 gauge galvanized steel with weatherproof locking cover and hardware for surface mounting as required for Project. Dimensions as required for Project.

Test mandrel: shall be ¼ inch smaller than inside conduit diameter and minimum 12 inches long.

Pull-rope: ¼-inch Nylon pull rope.

Core Drill Seals for Outside Building Walls: Link-Seal waterproof assembly or equal. Manufactured by PSI/Thunderline/Link-Seal.

Conduit Caulking Compound: Choose compounds for sealing conduit ducts that have putty-like consistency workable with hands, at temperatures as low as 35 degrees Fahrenheit, do not slump at a temperature of 300 degrees Fahrenheit, and do not harden materially when exposed to air. Compounds shall readily caulk or adhere to clean surfaces of plastic conduit, metallic conduits, or conduit coatings; concrete, masonry; any cable sheaths, jackets, covers or insulation material and common metals. Compounds shall form a seal without dissolving, noticeably changing characteristics, or removing any of the ingredients. Compounds shall have no injurious effect on the hands of workers or upon materials.

Underground Plastic Line marker: Manufacturer’s standard permanent, continuous-printed polyethylene film tape with metallic core, intended for direct burial service; not less than 3 inches wide x 4 mils thick. Provide orange tape with black text reading, “CAUTION FIBER OPTIC CABLE BELOW”.

Ground Wire: Bare Copper # 6

Tracer Box: NEMA-3 4-inch x 4-inch weatherproof box

Spacers for 4-inch Conduit: Carlon S289NJN Intermediate Spacer and S288NJN Base Spacer.

Precast Concrete Vault:

General: Provide precast concrete communications vault as detailed on the Drawings and as required for installation of new duct-bank systems and connection to existing duct-bank systems at locations shown on the Drawings. Provide 4-foot x 8-foot x 6-foot deep precast.

Design: Vaults shall be steel reinforced and the complete vault assembly designed for H‑20‑44 bridge loading. Clearly indicate in submittals all dimensions and reinforcing steel.

Concrete: Construct vaults using concrete with a 4500 psi 28-day strength. Concrete mix shall be designed in accordance with ASTM standards.

Reinforcing Steel: Use intermediate or hard grade billet steel conforming to ASTM A15, deformed in accordance with ASTM A305.

Vaults: Vault and pull box covers for all non-traffic areas shall be made of ductile iron cover; covers in parking and traffic areas shall be cast iron and rated for heavy vehicular traffic. Mount covers in a 30-inch Type "B" or "WRM" frame. Dowel the frame and neck into the vault to prevent movement away from the opening. Mark voice and data communications vaults and pull box covers with the text "TELECOMMUNICATIONS".

Conduit Entry: For plastic conduits, include a bell end inside the vault or pull box, mounted flush and grouted to seal openings. Provide precast fiber type terminators for each duct-bank entry.

Grounding: A #4/0 bare copper ground wire shall penetrate the side wall in the bottom section of each vault and pull box and extend 48 inches inside and outside of the vault pull box.

Accessories: Provide knockouts, cable racks, sumps, steps, joint seals and other accessories shown on the Drawings or as required for a complete installation.

Duct Plug 4-inch: General Machine Products (GMP) 6668R16

End Bell 4-inch: Carlon E297N

Multi-cell Fabric Mesh Duct:

Manufacturer: MaxCell.

Use only manufacturer’s fittings, transition adapters, terminators, accessories and installation kits.

* + - * 1. CABLE ROUTING HARDWARE

Cable Rack with Support Hardware as required (or comparable):

18-Hole: Condux 08380200, Chance C203-1126

Other sizes as required: Condux, Chance

Cable Rack Steps/Hooks:

4-inch: Condux 08380600, Chance C203-1131

Other sizes as required: Condux, Chance

“S” Rack Supports: Condux, Chance

Step Lock Wedge: Panduit CHW-C20

1. EXECUTION
   * + 1. INSPECTION
          1. Examine areas and conditions under which the new exterior telecommunications pathways are to be installed.
          2. Verify field measurements and pathway routing conditions are as shown on Drawings.
          3. If discrepancies or problems are found, notify Architect, and wait for direction. Beginning of telecommunications pathway installation indicates Contractor acceptance of existing conditions.
       2. EXCAVATING, TRENCHING AND BACKFILLING:
          1. General: The Work hereunder includes excavation and backfill as necessary to install the voice and data communications work. Coordinate voice and data communications work with other work in the same area, including excavating and backfilling, dewatering, floor protection provisions, other temporary facilities, other underground services (existing and new), landscape, paving, structural foundations and floor slabs on grade. Coordinate with weather conditions and provide temporary facilities needed for protection and proper performance of excavating and backfilling.
          2. Standards: Comply with the applicable provisions of *Division 31 Trenching, Backfilling, and Compaction*. Refer instances of uncertain applicability to the Architect/Engineer for resolution before proceeding with the Work.
          3. Refer to Owner before cutting or drilling any surface.
          4. All utilities are to be located by Contractor and exposed, if necessary, prior to construction.
          5. Before excavation, notify UITNS PM of work to be done so that service interruptions in existing fiber pathways can be prevented. A UIT employee must be present during excavation.
          6. Voice and data communications duct-banks shall be independent and not shared with any other systems.
          7. Accurately excavate the bottom of the trench to provide firm, uniform bearing for the bottom of raceways and duct-banks. Where mud or unstable soil is encountered in bottom of trench, remove it to firm bearing and backfill the trench with bedding sand to proper grade and tamp to provide uniform firm support.
          8. Accurately grade the bottom of trenches to provide proper fall and uniform bearing and support for each section of the conduit on undisturbed soil or 2 inches of sand fill at every point along its entire length. In general, grading for voice and data communications duct-banks and conduits shall be from building to vault, and from a high point between vaults to each vault.
          9. Exercise care not to excavate below required depth, leaving a flat bed of undisturbed earth, firm and secure, before laying conduit. In the event rock is encountered, excavate 6 inches below required depth and backfill to required depth with bedding sand, and compact to minimum 95% compaction.
          10. Control all grading in the vicinity of excavation to prevent surface ground water from flowing into the excavations. Remove any water accumulated in the excavations by pumping or other acceptable method. During excavation, stack material suitable for backfilling in an orderly manner, a sufficient distance back from edges of trenches to avoid overloading and prevent slides or cave-ins. Material unsuitable for backfilling shall be removed from the site and properly disposed of.
          11. If any unknown and/or uncharted utilities are encountered during excavation, promptly notify Architect/Engineer and wait for instructions before proceeding.
          12. If unknown utilities are encountered and work is continued without contacting the Architect/Engineer for instructions, and damage is caused to said utilities, the Contractor shall repair such damage, at his own expense, to the satisfaction of the Owner or utility company concerned.
          13. Do not backfill trenches until all required tests have been made by the Contractor and approved by the Architect/Engineer.
          14. Backfill shall be cement stabilized sand up to 6 inches above the top of conduit or duct-bank. Backfill up to grade shall be in maximum 6-inch lifts with minimum 95% compaction of lifts. *Refer to Division 31 Trenching, Backfilling, and Compaction* for additional requirements.
          15. Opening and Re-closing Pavement, Landscape Areas and Lawns: Where excavation requires the opening of existing walks, street, drives, other existing pavement or lawns, such surfaces shall be cut as required to install new conduit and to make new connections to existing conduits. The sizes of the cut shall be held to a minimum, consistent with the work to be accomplished. After installation of the new work is completed and the excavation has been backfilled and flooded, the area shall be patched or replaced, using materials to match those cut out or removed. Patches shall thoroughly bond with the original surfaces, be level with them.
          16. Excavation in Vicinity of Trees: The Contractor shall comply with applicable requirements as stated in *Division 31 Site Preparation,* and on the tree protection Drawings.
          17. Perform all trenching and backfill for new underground conduit system placement as shown on the Drawings.
          18. Perform pavement marking as required.
       3. CONDUIT SYSTEM PLACEMENT
          1. Place new conduit system including maintenance holes as shown on the Drawings.
          2. Maintain 12-inch clearance from all utilities. Conduit is to be encased in concrete slurry (flow fill) where proper distance cannot be obtained.
          3. Cross telecommunications conduit ducts below gas piping.
          4. Thoroughly clean all conduits before laying or using.
          5. During construction, plug the ends of the conduits to prevent water washing mud into the conduits, vaults or buildings. Take particular care to keep the conduits clean of concrete, dirt or any other substance during the construction.
          6. New and reopened trenches under asphalt roadways and parking lots shall have concrete cap or be encased in concrete as required.
          7. Support multiple conduits on preformed nonmetallic separators to provide not less than 1-inch spacing between exterior surfaces of conduit (Type 5). Space separators close enough to prevent sagging of conduits or breaking of couplings and watertight seals.
          8. Place moistened pea-sized gravel and sand mixture in the trench for 20 feet on each side of the vaults (Type 4).
          9. Multi-cell Fabric Mesh Duct:

Install all fabric mesh duct per manufacturer’s requirements.

Populate all fabric mesh duct with a measured pull tape.

* + - * 1. Securely anchor conduits in place with nylon tie-downs to prevent movement during the placement of concrete slurry (flow fill), moistened pea-sized gravel and sand mixture, and other backfill materials. Wire tie-downs are prohibited.
        2. Conduit Joint Couplings:

Install PVC non-metallic fittings with solvent applied couplings.

Use an approved transition coupling to connect metal to plastic (PVC) conduits.

* + - * 1. Couplings may be threaded and/or glued to provide watertight seal at conduit junctions.
        2. Seal all conduit junctions and fittings watertight prior to pour of concrete slurry (flow fill). Make conduit couplings in accordance with the manufacturer’s recommendation for the particular type of conduit and coupling selected and as approved.
        3. Unless otherwise noted on Drawings, a minimum 24-inch depth of cover is required above the top of all conduits.
        4. Provide communications drain box in conduit 6 feet from building outside wall penetrations as shown in Drawings. Perforate conduit inside drain box to allow water and gas to escape.
        5. Transition to PVC coated Galvanized Rigid Conduit (GRC) at 5 feet from building outside wall penetrations.
        6. For all offsets and sweep bends, provide fiberglass or PVC coated GRC.
        7. All conduit bends are to be minimum 3-foot radius or larger as noted on Drawings.
        8. Bury underground plastic line marker 12 inches above the telecommunications conduit.
        9. Cast into concrete a #6 bare copper ground wire directly above the telecommunications conduit and extend 4 inches into each vault space. Extend 6 inches of tracer wire into tracer box on outside wall of building directly above conduit entry point.
        10. Provide plastic conduit bell ends at each PVC conduit termination and for all conduit entering vaults.
        11. Avoid boring under concrete sidewalks. Remove and replace sidewalks as necessary.
        12. Extend the new conduit through the wall into the building, tunnel, or crawl space a minimum of 4 inches.
        13. Building, tunnel and vault core drills shall be sealed around conduits with approved waterproof plugging compound.

Seal openings around conduits that pass through inside building wall core drills with UL listed foamed silicone elastomeric compound.

Seal openings around conduits that pass through outside building walls with a complete Link-Seal assembly for a waterproof seal. Slope conduit away from building.

Seal openings around conduits that pass through vault walls with foundation foam on the interior of the core and silicone sealer on the inside and outside of the core for a waterproof seal.

* + - * 1. Place Maintenance Holes (MH) with the long dimension in line with the main conduit run. The conduit shall enter opposite ends of the MH on the short sides. Do not use the MH as a 90 degree bend in cable installations.
        2. Ream and bush the ends of the metallic conduit:

Insulated metallic bushings for 1 ¼-inch conduit and larger

Insulated metallic bushings with grounding lugs for conduit entering Network Facilities (NFs).

* + - * 1. After conduit duct installation has been completed and concrete has set, pull “D” test mandrel through all new conduit ducts to verify duct integrity and ensure smooth interior surfaces free from burrs or obstructions that might damage cable sheaths.
        2. Following mandrel testing, draw cylindrical wire brush with stiff bristles through each conduit to clean the conduit and remove any concrete, dirt or other obstructions.
        3. Stub out conduits into NFs, and cabinets only enough to attach connector and bushings with grounding lugs, except conduits shall rise a minimum of 6 inches above the finished floor.
        4. Install new pull rope in all new conduit and extend three feet into each building space.
        5. Plug ends of the new conduit with watertight rubber conduit plugs, conduit caulking compound or conduit caps to ensure foreign matter does not enter the buildings.
      1. CABLE ROUTING HARDWARE
         1. Place new cable routing hardware in the tunnels and in crawl spaces beneath the building as required and as shown on the Drawings.
         2. Perform installation of routing hardware including anchoring and supports, grounding and bonding as specified in *Section 27 0526 Grounding and Bonding for Communications Systems*.
         3. Place new ladder, pulling-in irons, cable racks, “S” rack supports, and steps in new and existing vaults as required for backbone cable routing.
      2. HORIZONTAL DIRECTIONAL DRILLING
         1. Notify Owner atleast 48 hours in advance of starting horizontal directional drilling work. Do not begin the directional drilling until Owner is present at the job site and agrees that proper preparations have been made.
         2. No work can commence until Traffic Control and Construction Permits are in place.
         3. Site Preparation

Prior to any alterations to work site, mark the entry and exit points.

Make no alterations to the work site beyond what is required for operations.

Confine all activities to designated work areas.

* + - * 1. Drill Path Survey

Accurately survey the entire drill path with entry and exit stakes placed in the appropriate locations within the areas indicated on Drawings.

If a magnetic guidance system is being used, the drill path shall be surveyed for any surface geomagnetic variations or anomalies.

* + - * 1. Following drilling operations, the equipment shall be de-mobilized and the worksite restored to its original condition.
      1. SAFETY
         1. Adhere to all applicable state, federal and local safety regulations and conduct all operations in a safe manner.
         2. The Contractor shall comply with UH Environmental Health & Life Safety procedures as stated in <https://uh.edu/ehls/about/manuals/>.

END OF SECTION 27 0543