## BDF Check list
PRIORITY |  |  | LEGACY MINIMUM | UHS IT STANDARD
| GENERAL | DATE / TIME |  |  | DATE AND TIME
|  | INSPECTOR NAME |  |  | #
|  | CAMPUS |  |  | CLEAR LAKE | DOWNTOWN | MAIN | VICTORIA
|  | BUILDING |  |  | TEXT
|  | ROOM TYPE | LEGACY OR LEGACY CIR | STANDARD OR STANDARD CIR | STANDARD | LEGACY | STANDARD CIR | STANDARD CIR
|  | ROOM NUMBER |  |  | TEXT
HIGH |  | TEMPERATURE | 60 - 75F | 60 - 75F | #
HIGH |  | HUMIDITY | 30 - 50% RH | 30 - 50% RH | #
HIGH |  | ASSET TAG ON DOOR FRAME | YES | YES | # | NONE
MED |  | CONTROLLABLE THERMOSTAT | YES | YES | YES | NOT CONTROLLABLE | NONE IN ROOM
|  |  | LEGACY MINIMUM | UHS IT STANDARD
HIGH | ROOM INFORMATION | ROOM OWNER | SHARED OR IT | IT | IT | SHARED | SHARED MOSTLY OTHERS
HIGH |  | SPACE USE | DEDICATED OR APPROVED MULTI-USE | DEDICATED (IT) | DEDICATED (IT) | APPROVED MULTI-USE | UTILITY / MECHANICAL | OTHER
HIGH |  | ACCESS | READER W/ IT MASTER KEY | READER W/ IT MASTER KEY | READER W/ IT MASTER KEY | IT MASTER KEYED | COMMON KEYED | NONE
HIGH |  | CAMERA INTERIOR | YES | YES | YES | NO |  | NON OPERATIONAL
HIGH |  | CAMERA EXTERIOR | YES OR NOT REQURED | YES OR NOT REQUIRED | YES | NO | NOT REQUIRED | NON OPERATIONAL
HIGH |  | DOOR TYPE | SOLID | SOLID | SOLID | LOUVERED | GLASS
MED |  | ROOM LABEL | YES | YES | YES | NO
MED |  | DOOR SWING | DOES NOT AFFECT ROOM USE | OUT | OUT | IN | AFFECTS ROOM USE
HIGH |  | LIGHTING | OPERATIONAL | SWITCH | SWITCH | MOTION | NONE | SWITCH NON OPERATIONAL | MOTION NON OPERATIONAL
HIGH |  | WALLS TO DECK | YES | YES | YES | NO
LOW |  | CEILING | ANY | OPEN/NONE | OPEN/NONE | SHEETROCK | CEILING TILE
|  | FIRE SUPPRESSION | ANY | PRE-ACTION | BUILDING STANDARD | PRE-ACTION | CLEAN AGENT | NONE (EXTIGUISHER REQ)
LOW |  | SPRINKLER HEADS | CAGED | CAGED | CAGED | NOT CAGED | NONE
HIGH |  | INSPECTED FIRE EXTINGUISHER | IF NO FIRE SUPPRESSION | NOT REQUIRED | NOT REQUIRED | CO2 OR CLEAN AGENT | WET TYPE (REPLACE) | INSPECTION REQUIRED
HIGH |  | POWER CORD TRIPPING HAZARD | NO | NO | NO | YES
|  |  | LEGACY MINIMUM | UHS IT STANDARD
LOW | HOUSE KEEPING | TRASH IN ROOM | NO | NO | NO | YES, REMOVE
LOW |  | FLOOR IS CLEAN | YES | YES | YES | NO, CLEANING REQUIRED
LOW |  | EQUIPMENT DUST FREE | YES | YES | YES | NO , CLEANING REQUIRED
MED |  | INAPROPRIATE STORAGE | NO | NO | NO | YES
HIGH |  | ABANDONED CABLING | NO | NO | NO | YES
|  |  | LEGACY MINIMUM | UHS IT STANDARD
HIGH | NON SERVICING SYSTEMS | WATER PIPES | NO OR DRIP PAN INSTALLED | NO | NO | YES, DRIP PAN INSTALLED | YES, DRIP PAN NEEDED
HIGH |  | SEWER PIPES | NO OR DRIP PAN INSTALLED | NO | NO | YES, DRIP PAN INSTALLED | YES, DRIP PAN NEEDED
HIGH |  | FIRE MAIN | NO OR DRIP PAN INSTALLED | NO | NO | YES, DRIP PAN INSTALLED | YES, DRIP PAN NEEDED
HIGH |  | ROOF DRAINS | NO OR DRIP PAN INSTALLED | NO | NO | YES, DRIP PAN INSTALLED | YES, DRIP PAN NEEDED
HIGH |  | ELECTRICAL PANELS | NO OR SERVICES ROOM | NO OR SERVICES ROOM | NO | YES, SERVICES ROOM | YES, NOT APPROVED BY IT
HIGH |  | ACCESS CONTROL PANELS | NO OR IF APPROVED BY IT | NO OR IF APPROVED BY IT | NO | YES, APPROVED BY IT | YES, NOT APPROVED BY IT
HIGH |  | AV SYSTEMS | NO OR YES, IF APPROVED BY IT | NO OR IF APPROVED BY IT | NO | YES, APPROVED BY IT | YES, NOT APPROVED BY IT
|  |  | LEGACY MINIMUM | UHS IT STANDARD
MED | ROOM CABLE SUPPORT | OVERHEAD CABLE SUPPORT | ANY (NOT NONE) | BASKET OR LADDER | BASKET | LADDER | HOOKS | NONE, SUPPORT REQUIRED
MED |  | WALL CABLE SUPPORT | ANY (NOT NONE) | LADDER | BASKET | LADDER | D-RINGS | NONE, SUPPORT REQUIRED
MED |  | SUPPORT CAPACITY | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | TRAY FULL | REWORK REQUIRED
LOW |  | CABLE TRAY DRESSING | NEAT AND TIDY | NEAT AND TIDY | NEAT AND TIDY | REDRESSING REQUIRED
HIGH |  | HORIZONTAL PENETRATIONS | COMPLIANT OR SEALED | FIRE-STOP COMPLIANT | FIRE-STOP COMPLIANT | FIRE-STOP NON COMPLIANT | PENETRATIONS SEALED | PENETRATIONS NOT SEALED
MED |  | HORZ. PENETRATION SPACE | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | FULL | OVERFILLED
HIGH |  | VERTICAL PENETRATIONS | FIRE-STOP COMPLIANT | FIRE-STOP COMPLIANT | FIRE-STOP COMPLIANT | FIRE-STOP NON COMPLIANT | NOT APPLICABLE
MED |  | VERTL PENETRATION SPACE | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | FULL | OVERFILLED
HIGH |  | INCOMMING OSP CONDUIT | FIRE-STOP COMPLIANT | FIRE-STOP COMPLIANT | FIRE-STOP COMPLIANT | FIRE-STOP NON COMPLIANT | PENETRATIONS SEALED | PENETRATIONS NOT SEALED
MED |  | OSP CONDUIT SPACE | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | FULL | OVERFILLED
|  |  | LEGACY MINIMUM | UHS IT STANDARD
HIGH | MEP | LIGHTS | EMERGENCY | EMERGENCY | EMERGENCY | HOUSE POWER | UNKNOWN SUFFICIENT | NOT SUFFICIENT
HIGH |  | HVAC | DEDICATED | DEDICATED | DEDICATED | BUILDING AIR | NONE | UNKNOWN
|  | HVAC TYPE | N/A | N/A | CHILLED WATER | DX | BOTH | UNKNOWN
MED |  | WALL POWER | EMERGENCY OR HOUSE | EMERGENCY | EMERGENCY | HOUSE POWER | NONE | UNKNOWN
HIGH |  | RACK POWER -TWIST LOCK | EMERGENCY OR HOUSE | EMERGENCY | EMERGENCY | HOUSE POWER | NONE
HIGH |  | RACK POWER - NON LOCKING | EMERGENCY OR HOUSE | EMERGENCY | EMERGENCY | HOUSE POWER | NONE
MED |  | POSITIVE PRESSURE | YES | YES | YES | NO
|  |  | LEGACY MINIMUM | UHS IT STANDARD
HIGH | GROUNDING AND BONDING | 24" X 4" TMGB OR PBB | YES | YES | YES | NO | UNDERSIZED
HIGH |  | TWO HOLE TUGS USED | YES | YES | YES | NO
HIGH |  | TRAY BONDED TO TGB | YES | YES | YES | NO
HIGH |  | RACK BONDED TO TGB | YES | YES | YES | NO
HIGH |  | UPS BONDED TO RACK | YES | YES | YES | NO
HIGH |  | PDU(S) BONDED TO RACK | YES OR NA | YES | YES | NO | NA
HIGH |  | OSP CABLE EQUIPMENT | YES | YES | YES | NO | NA
|  |  | LEGACY MINIMUM | UHS IT STANDARD
| RACK RELATED | NUMBER OF RACKS / CABINETS | SPARE RACK UNITS REQUIRED | 4 | 1 | 2 | 3 | 4
MED |  | RACK 1 SPARE RACK UNITS | 5 RU OR MORE | 5RU OR MORE | #
MED |  | RACK 2 SPARE RACK UNITS |  |  | #
MED |  | RACK 3 SPARE RACK UNITS |  |  | #
MED |  | RACK 4 SPARE RACK UNITS |  |  | #
MED |  | SPARE PATCH PANEL PORTS | 6 OR MORE | 6 OR MORE | # | #
LOW |  | VERTICAL MANAGERS | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | REDRESSING REQUIRED | FULL | NONE
LOW |  | HORIZONTAL MANAGERS | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | REDRESSING REQUIRED | FULL | NONE
HIGH |  | FRONT CLEARANCE | NOT UNSAFE | 3FT+ | 3FT+ | 2FT+ | NONE | UNSAFE
HIGH |  | REAR CLEARANCE | NOT UNSAFE | 3FT+ | 3FT+ | 2FT+ | NONE | UNSAFE
LOW |  | ROOM FOR ADDITIONAL RACK | YES OR EMPTY RACKS AVAILABLE | YES OR EMPTY RACKS AVAILABLE | YES | NO, EMPTY RACK(S) AVAILABLE | NONE
|  |  | LEGACY MINIMUM | UHS IT STANDARD
| UPS | UPS SIZE | N/A | N/A | 1500W | 5000W | 3000W | NONE
HIGH |  | UPS STATUS | PASSED TEST | PASSED TEST | PASSED TEST | FAILS TEST | NONE
MED |  | UPS MONITORED | YES | YES | YES | NO
MED |  | ROOM TEMP MONITORING | YES | YES | YES | NO
|  | STEP DOWN TRANSFORMER (UHD) | ANY | ANY | YES | NO | NA
|  |  | LEGACY MINIMUM | UHS IT STANDARD
LOW | LABELING | ROOM | YES | YES | YES | NO
LOW |  | RACKS | YES | YES | YES | NO
LOW |  | FIBER CABLE | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | FIBER PANEL | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | BACKBONE COPPER CABLE | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | BACKBONE COPPER PANEL | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | HORIZONTAL CABLE | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | HORIZONTAL PATCH PANEL | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | SWITCHES | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | UPS | YES | YES | YES | NO | UPDATE REQUIRED
HIGH |  | BUSS BAR | YES | YES | YES | NO | UPDATE REQUIRED
HIGH |  | FIRE STOP ASSEMBLIES | YES | YES | YES | NO | UPDATE REQUIRED
|  |  | LEGACY MINIMUM | UHS IT STANDARD
| BACKBONE | FIBER CABLE MFG | BUILDING SPECIFIC | BUILDING SPECIFIC | COMMSCOPE | CORNING | PYRSMIAN | DRAKA
|  | FIBER CONNECTIVITY | BUILDING SPECIFIC | LC OR APC | LC | ST | APC | SC
MED |  | FIBER AT CAPACITY | NO | NO | YES | NO
|  | BACKBONE COPPER CABLE | ANY | ANY | 25 PAIR | 50 PAIR | 100 PAIR | NONE
MED |  | COPPER BACKBONE AT CAPACITY | NO | NO | YES | NO
|  |  | LEGACY MINIMUM | UHS IT STANDARD
| HORIZ. COPPER | HORIZONTAL CABLE MFG | BUILDING SPECIFIC | BUILDING SPECIFIC | COMMSCOPE | PANDUIT / GENERAL | BERKTEK | ICC | OTHER
|  | HORIZONTAL CONNECTIVITY | BUILDING SPECIFIC | BUILDING SPECIFIC | COMMSCOPE | PANDUIT | LEVITON | ICC | OTHER
MED |  | CATEGORY | CATEGORY 6 OR BETTER | CATEGORY 6 OR BETTER | CATEGORY 3 | CATEGORY 5 / 5E | CATEGORY 6/6E | CATEGORY 6A | COMBINATION
MED |  | SPARE PORTS ON PANEL | 6 OR MORE | 6 OR MORE | #
|  |  | LEGACY MINIMUM | UHS IT STANDARD
| COAX | RISER | ANY | NONE | 0.500 HARDLINE | RG-59 | RG-6 | NONE
LOW |  | HORIZONTAL COAX | ANY | NO | YES | NO |  | NONE

## MDF Checklist
|  |  | LEGACY MINIMUM | UHS IT STANDARD
| GENERAL | DATE / TIME |  |  | DATE AND TIME
|  | INSPECTOR NAME |  |  | #
|  | CAMPUS |  |  | CLEAR LAKE | DOWNTOWN | MAIN | VICTORIA
|  | BUILDING |  |  | TEXT
|  | ROOM TYPE | LEGACY OR LEGACY CIR | STANDARD OR STANDARD CIR | STANDARD | LEGACY | STANDARD CIR | STANDARD CIR
|  | ROOM NUMBER |  |  | TEXT
HIGH |  | TEMPERATURE | 60 - 75F | 60 - 75F | #
HIGH |  | HUMIDITY | 30 - 50% RH | 30 - 50% RH | #
HIGH |  | ASSET TAG ON DOOR FRAME | YES | YES | # | NONE
MED |  | CONTROLLABLE TERMOSTAT | YES | YES | YES | NOT CONTROLLABLE | NONE IN ROOM
|  |  | LEGACY MINIMUM | UHS IT STANDARD
HIGH | ROOM INFORMATION | ROOM OWNER | SHARED OR IT | IT | IT | SHARED | OTHERS
HIGH |  | SPACE USE | DEDICATED OR APPROVED MULTI-USE | DEDICATED (IT) | DEDICATED (IT) | APPROVED MULTI-USE | UTILITY / MECHANICAL | OTHER
HIGH |  | ACCESS | READER W/ IT MASTER KEY | READER W/ IT MASTER KEY | READER W/ IT MASTER KEY | IT MASTER KEYED | COMMON KEYED | NONE
HIGH |  | CAMERA INTERIOR | YES | YES | YES | NO |  | NON OPERATIONAL
CS |  | CAMERA EXTERIOR | YES OR NOT REQUIRED | YES OR NOT REQUIRED | YES | NO | NOT REQUIRED | NON OPERATIONAL
HIGH |  | DOOR TYPE | SOLID | SOLID | SOLID | LOUVERED | GLASS
MED |  | ROOM LABEL | YES | YES | YES | NO
MED |  | DOOR SWING | DOES NOT AFFECT ROOM USE | OUT | OUT | IN | AFFECTS ROOM USE
HIGH |  | LIGHTING | OPERATIONAL | SWITCH | SWITCH | MOTION | NONE | SWITCH NON OPERATIONAL | MOTION NON OPERATIONAL
HIGH |  | WALLS TO DECK | YES | YES | YES | NO
LOW |  | CEILING | ANY | OPEN/NONE | OPEN/NONE | SHEETROCK | CEILING TILE
|  | FIRE SUPPRESSION | ANY | PRE-ACTION | BUILDING STANDARD | PRE-ACTION | CLEAN AGENT | NONE (EXTIGUISHER REQ)
LOW |  | SPRINKLER HEADS | CAGED | CAGED | CAGED | NOT CAGED | NONE
HIGH |  | INSPECTED FIRE EXTINGUISHER | IF NO FIRE SUPPRESSION | NOT REQUIRED | NOT REQUIRED | CO2 OR CLEAN AGENT | WET TYPE (REPLACE) | INSPECTION REQUIRED
HIGH |  | SPACE FOR GROWTH | YES | YES | YES | NO
HIGH |  | SERVICE PROVIDER SECURITY | NO FREE ACCESS | DEDICATED OR CAGED | DEDICATED ROOM | CAGED SPACE | ESCORT REQUIRED | FREE ACCESS
|  |  | LEGACY MINIMUM | UHS IT STANDARD
LOW | HOUSE KEEPING | TRASH IN ROOM | NO | NO | NO | YES, REMOVE
LOW |  | FLOOR IS CLEAN | YES | YES | YES | NO, CLEANING REQUIRED
LOW |  | EQUIPMENT DUST FREE | YES | YES | YES | NO, CLEANING REQUIRED
MED |  | INAPROPRIATE STORAGE | NO | NO | NO | YES
HIGH |  | ABANDONED CABLING | NO | NO | NO | YES
|  |  | LEGACY MINIMUM | UHS IT STANDARD
HIGH | NON SERVICING SYSTEMS | WATER PIPES | NO OR DRIP PAN INSTALLED | NO | NO | YES, DRIP PAN INSTALLED | YES, DRIP PAN NEEDED
HIGH |  | SEWER PIPES | NO OR DRIP PAN INSTALLED | NO | NO | YES, DRIP PAN INSTALLED | YES, DRIP PAN NEEDED
HIGH |  | FIRE MAIN | NO OR DRIP PAN INSTALLED | NO | NO | YES, DRIP PAN INSTALLED | YES, DRIP PAN NEEDED
HIGH |  | ROOF DRAINS | NO OR DRIP PAN INSTALLED | NO | NO | YES, DRIP PAN INSTALLED | YES, DRIP PAN NEEDED
HIGH |  | ELECTRICAL PANELS | NO OR SERVICES ROOM | NO OR SERVICES ROOM | NO | YES, SERVICES ROOM | YES, NOT APPROVED BY IT
HIGH US |  | ACCESS CONTROL PANELS | NO OR IF APPROVED BY IT | NO OR IF APPROVED BY IT | NO | YES, APPROVED BY IT | YES, NOT APPROVED BY IT
HIGH US |  | AV SYSTEMS | NO OR YES, APPROVED BY IT | NO OR IF APPROVED BY IT | NO | YES, APPROVED BY IT | YES, NOT APPROVED BY IT
|  |  | LEGACY MINIMUM | UHS IT STANDARD
MED | ROOM CABLE SUPPORT | OVERHEAD CABLE SUPPORT | ANY (NOT NONE) | BASKET OR LADDER | BASKET | LADDER | HOOKS | NONE, SUPPORT REQUIRED
MED |  | WALL CABLE SUPPORT | ANY (NOT NONE) | LADDER | BASKET | LADDER | D-RINGS | NONE, SUPPORT REQUIRED
MED |  | SUPPORT CAPACITY | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | TRAY FULL | REWORK REQUIRED
LOW |  | CABLE TRAY DRESSING | NEAT AND TIDY | NEAT AND TIDY | NEAT AND TIDY | REDRESSING REQUIRED
HIGH |  | HORIZONTAL PENETRATIONS | COMPLIANT OR SEALED | FIRE-STOP COMPLIANT | FIRE-STOP COMPLIANT | FIRE-STOP NON COMPLIANT | PENETRATIONS SEALED | PENETRATIONS NOT SEALED
MED |  | HORZ. PENETRATION SPACE | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | FULL | OVERFILLED
HIGH |  | VERTICAL PENETRATIONS | FIRE-STOP COMPLIANT | FIRE-STOP COMPLIANT | FIRE-STOP COMPLIANT | FIRE-STOP NON COMPLIANT | NOT APPLICABLE
MED |  | VERTL PENETRATION SPACE | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | FULL | OVERFILLED
HIGH |  | INCOMMING OSP CONDUIT | FIRE-STOP COMPLIANT | FIRE-STOP COMPLIANT | FIRE-STOP COMPLIANT | FIRE-STOP NON COMPLIANT | PENETRATIONS SEALED | PENETRATIONS NOT SEALED
MED |  | OSP CONDUIT SPACE | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | FULL | OVERFILLED
|  |  | LEGACY MINIMUM | UHS IT STANDARD
HIGH* | MEP | LIGHTS | EMERGENCY | EMERGENCY | EMERGENCY | HOUSE POWER | UNKNOWN SUFFICIENT | NOT SUFFICIENT
HIGH* |  | HVAC | DEDICATED | DEDICATED | DEDICATED | BUILDING AIR | NONE | UNKNOWN
|  | HVAC TYPE | ANY | ANY | CHILLED WATER | DX | BOTH | UNKNOWN
MED |  | WALL POWER | EMERGENCY OR HOUSE | EMERGENCY | EMERGENCY | HOUSE POWER | NONE | UNKNOWN
HIGH |  | RACK POWER -TWIST LOCK | EMERGENCY | EMERGENCY | EMERGENCY | HOUSE POWER | NONE
HIGH |  | RACK POWER - NON LOCKING | EMERGENCY | EMERGENCY | EMERGENCY | HOUSE POWER | NONE
MED |  | POSITIVE PRESSURE | YES | YES | YES | NO
HIGH |  | SERVICE PROVIDER | EMERGENCY | EMERGENCY | EMERGENCY | HOUSE POWER | NONE | UNKNOWN
|  |  | LEGACY MINIMUM | UHS IT STANDARD
HIGH | GROUNDING AND BONDING | 24" X 4" TMGB OR PBB | YES | YES | YES | NO | UNDERSIZED
HIGH |  | TWO HOLE TUGS USED | YES | YES | YES | NO
HIGH |  | TRAY BONDED TO TGB | YES | YES | YES | NO
HIGH |  | RACK BONDED TO TGB | YES | YES | YES | NO
HIGH |  | UPS BONDED TO RACK | YES | YES | YES | NO
HIGH |  | PDU(S) BONDED TO RACK | YES | YES | YES | NO | NA
HIGH |  | OSP CABLE EQUIPMENT | YES | YES | YES | NO | NA
HIGH |  | SERVICE PROVIDER EQUIPMENT | YES | YES | YES | NO
|  |  | LEGACY MINIMUM | UHS IT STANDARD
| RACK RELATED | NUMBER OF RACKS / CABINETS | SPARE RACK UNITS REQUIRED |  | #
MED |  | RACK 1 SPARE RACK UNITS | 5 RU OR MORE |  | #
MED |  | RACK 2 SPARE RACK UNITS |  |  | #
MED |  | RACK 3 SPARE RACK UNITS |  |  | #
MED |  | RACK 4 SPARE RACK UNITS |  |  | #
MED |  | SPARE PATCH PANEL PORTS | 6 OR MORE | 6 OR MORE | # | #
LOW |  | VERTICAL MANAGERS | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | REDRESSING REQUIRED | FULL | NONE
LOW |  | HORIZONTAL MANAGERS | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | REDRESSING REQUIRED | FULL | NONE
HIGH |  | FRONT CLEARANCE | NOT UNSAFE | 3FT+ | 3FT+ | 2FT+ | NONE | UNSAFE
HIGH |  | REAR CLEARANCE | NOT UNSAFE | 3FT+ | 3FT+ | 2FT+ | NONE | UNSAFE
LOW |  | ROOM FOR ADDITIONAL RACK | YES OR EMPTY RACKS AVAILABLE | YES OR EMPTY RACKS AVAILABLE | YES | NO, EMPTY RACK(S) AVAILABLE | NONE
|  |  | LEGACY MINIMUM | UHS IT STANDARD
| UPS | UPS SIZE | N/A | N/A | 1500W | 5000W | 3000W | NONE
HIGH |  | UPS STATUS | PASSED TEST | PASSED TEST | PASSED TEST | FAILS TEST | NONE
MED |  | UPS MONITORED | YES | YES | YES | NO
MED |  | ROOM TEMP MONITORING | YES | YES | YES | NO
|  | STEP DOWN TRANSFORMER | ANY | ANY | YES | NO | NA
|  |  | LEGACY MINIMUM | UHS IT STANDARD
LOW | LABELING | ROOM | YES | YES | YES | NO
LOW |  | RACKS | YES | YES | YES | NO
LOW |  | FIBER CABLE | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | FIBER PANEL | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | BACKBONE COPPER CABLE | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | BACKBONE COPPER PANEL | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | HORIZONTAL CABLE | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | HORIZONTAL PATCH PANEL | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | SWITCHES | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | UPS | YES | YES | YES | NO | UPDATE REQUIRED
HIGH |  | BUSS BAR | YES | YES | YES | NO | UPDATE REQUIRED
HIGH |  | FIRE STOP ASSEMBLIES | YES | YES | YES | NO | UPDATE REQUIRED
|  |  | LEGACY MINIMUM | UHS IT STANDARD
| BACKBONE | FIBER CABLE MFG | BUILDING SPECIFIC | BUILDING SPECIFIC | COMMSCOPE | CORNING | PYRSMIAN | DRAKA | #
|  | FIBER CONNECTIVITY | ANY | LC | LC | ST | APC | SC | COMBINATION
MED |  | FIBER AT CAPACITY | NO | NO | ALL LINKS HAVE SPARES | SOME LINKS AT CAPACITY | MANY LINKS AT CAPACITY
|  | BACKBONE COPPER CABLE | ANY | 110 | 66 BLOCKS | 110 BLOCKS | 66 PROTECTORS | 110 PROTECTORS | COMBINATION
MED |  | COPPER BACKBONE AT CAPACITY | NO | NO | ALL LINKS HAVE SPARES | SOME LINKS AT CAPACITY | MANY LINKS AT CAPACITY
|  |  | LEGACY MINIMUM | UHS IT STANDARD
| HORIZ. COPPER | HORIZONTAL CABLE MFG |  |  | COMMSCOPE | PANDUIT / GENERAL | BERKTEK | ICC | OTHER
|  | HORIZONTAL CONNECTIVITY | BUILDING SPECIFIC | BUILDING SPECIFIC | COMMSCOPE | PANDUIT | LEVITON | ICC | OTHER
MED |  | CATEGORY | CATEGORY 6 OR BETTER | CATEGORY 6 OR BETTER | CATEGORY 3 | CATEGORY 5 / 5E | CATEGORY 6/6E | CATEGORY 6A | COMBINATION
MED |  | SPARE PORTS ON PANEL | 6 OR MORE | 6 OR MORE | #
|  |  | LEGACY MINIMUM | UHS IT STANDARD
| COAXIAL | RISER | ANY | NONE | 0.500 HARDLINE | RG-59 | RG-6
LOW |  | HORIZONTAL COAX | ANY | NO | YES | NO

## IDF Check list
|  |  | LEGACY MINIMUM | UHS IT STANDARD
| GENERAL | DATE / TIME |  |  | DATE AND TIME
|  | INSPECTOR NAME |  |  | #
|  | CAMPUS |  |  | CLEAR LAKE | DOWNTOWN | MAIN | VICTORIA
|  | BUILDING |  |  | TEXT
|  | ROOM TYPE | LEGACY OR LEGACY CIR | STANDARD OR STANDARD CIR | STANDARD | LEGACY | STANDARD CIR | STANDARD CIR
|  | ROOM NUMBER |  |  | TEXT
HIGH |  | TEMPERATURE | 60 - 75F | 60 - 75F | #
HIGH |  | HUMIDITY | 30 - 50% RH | 30 - 50% RH | #
HIGH |  | ASSET TAG ON DOOR FRAME | YES | YES | # | NONE
MED |  | CONTROLLABLE THERMOSTAT | YES | YES | YES | NOT CONTROLLABLE | NONE IN ROOM
|  |  | LEGACY MINIMUM | UHS IT STANDARD
HIGH | ROOM INFORMATION | ROOM OWNER | SHARED OR IT | IT | IT | SHARED | OTHERS
HIGH |  | SPACE USE | DEDICATED OR APPROVED MULTI-USE | DEDICATED (IT) | DEDICATED (IT) | APPROVED MULTI-USE | UTILITY / MECHANICAL | OTHER
HIGH |  | ACCESS | READER W/ IT MASTER KEY | READER W/ IT MASTER KEY | READER W/ IT MASTER KEY | IT MASTER KEYED | COMMON KEYED | NONE
HIGH |  | CAMERA INTERIOR | YES | YES | YES | NO |  | NON OPERATIONAL
HIGH |  | CAMERA EXTERIOR | YES OR NOT REQUIRED | YES OR NOT REQUIRED | YES | NO | NOT REQUIRED | NON OPERATIONAL
HIGH |  | DOOR TYPE | SOLID | SOLID | SOLID | LOUVERED | GLASS
MED |  | ROOM LABEL | YES | YES | YES | NO
MED |  | DOOR SWING | DOES NOT AFFECT ROOM USE | OUT | OUT | IN | AFFECTS ROOM USE
HIGH |  | LIGHTING | OPERATIONAL | SWITCH | SWITCH | MOTION | NONE | SWITCH NON OPERATIONAL | MOTION NON OPERATIONAL
HIGH |  | WALLS TO DECK | YES | YES | YES | NO
LOW |  | CEILING | ANY | OPEN/NONE | OPEN/NONE | SHEETROCK | CEILING TILE
|  | FIRE SUPPRESSION | ANY | PRE-ACTION | BUILDING STANDARD | PRE-ACTION | CLEAN AGENT | NONE (EXTIGUISHER REQ)
LOW |  | SPRINKLER HEADS | CAGED | CAGED HIGH TEMP | CAGED HIGH TEMP | NOT CAGED | NONE
HIGH |  | INSPECTED FIRE EXTINGUISHER | IF NO FIRE SUPPRESSION | NOT REQUIRED | NOT REQUIRED | CO2 OR CLEAN AGENT | WET TYPE (REPLACE) | INSPECTION REQUIRED
HIGH |  | POWER CORD TRIPPING HAZARD | NO | NO | NO | YES
|  |  | LEGACY MINIMUM | UHS IT STANDARD
LOW | HOUSE KEEPING | TRASH IN ROOM | NO | NO | NO | YES, REMOVE
LOW |  | FLOOR IS CLEAN | YES | YES | YES | NO, CLEANING REQUIRED
LOW |  | EQUIPMENT DUST FREE | YES | YES | YES | NO , CLEANING REQUIRED
MED |  | INAPROPRIATE STORAGE | NO | NO | NO | YES
HIGH |  | ABANDONED CABLING | NO | NO | NO | YES
|  |  | LEGACY MINIMUM | UHS IT STANDARD
HIGH | NON SERVICING SYSTEMS | WATER PIPES | NO OR DRIP PAN INSTALLED | NO | NO | YES, DRIP PAN INSTALLED | YES, DRIP PAN NEEDED
HIGH |  | SEWER PIPES | NO OR DRIP PAN INSTALLED | NO | NO | YES, DRIP PAN INSTALLED | YES, DRIP PAN NEEDED
HIGH |  | FIRE MAIN | NO OR DRIP PAN INSTALLED | NO | NO | YES, DRIP PAN INSTALLED | YES, DRIP PAN NEEDED
HIGH |  | ROOF DRAINS | NO OR DRIP PAN INSTALLED | NO | NO | YES, DRIP PAN INSTALLED | YES, DRIP PAN NEEDED
HIGH |  | ELECTRICAL PANELS | NO OR SERVICES ROOM | NO | NO | YES, SERVICES ROOM | YES, NOT APPROVED BY IT
HIGH |  | ACCESS CONTROL PANELS | NO OR IF APPROVED BY IT | NO OR IF APPROVED BY IT | NO | YES, APPROVED BY IT | YES, NOT APPROVED BY IT
HIGH |  | AV SYSTEMS | NO OR YES, APPROVED BY IT | NO OR IF APPROVED BY IT | NO | YES, APPROVED BY IT | YES, NOT APPROVED BY IT
|  |  | LEGACY MINIMUM | UHS IT STANDARD
MED | ROOM CABLE SUPPORT | OVERHEAD CABLE SUPPORT | ANY (NOT NONE) | BASKET OR LADDER | BASKET | LADDER | HOOKS | NONE, SUPPORT REQUIRED
MED |  | WALL CABLE SUPPORT | ANY (NOT NONE) | LADDER | BASKET | LADDER | D-RINGS | NONE, SUPPORT REQUIRED
MED |  | SUPPORT CAPACITY | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | TRAY FULL | REWORK REQUIRED
LOW |  | CABLE TRAY DRESSING | NEAT AND TIDY | NEAT AND TIDY | NEAT AND TIDY | REDRESSING REQUIRED
HIGH |  | HORIZONTAL PENETRATIONS | COMPLIANT OR SEALED | FIRE-STOP COMPLIANT | FIRE-STOP COMPLIANT | FIRE-STOP NON COMPLIANT | PENETRATIONS SEALED | PENETRATIONS NOT SEALED
MED |  | HORZ. PENETRATION SPACE | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | FULL | OVERFILLED
HIGH |  | VERTICAL PENETRATIONS | FIRE-STOP COMPLIANT | FIRE-STOP COMPLIANT | FIRE-STOP COMPLIANT | FIRE-STOP NON COMPLIANT | NOT APPLICABLE
MED |  | VERTL PENETRATION SPACE | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | FULL | OVERFILLED
HIGH |  | INCOMMING OSP CONDUIT | FIRE-STOP COMPLIANT | FIRE-STOP COMPLIANT | FIRE-STOP COMPLIANT | FIRE-STOP NON COMPLIANT | PENETRATIONS SEALED | PENETRATIONS NOT SEALED
MED |  | OSP CONDUIT SPACE | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | FULL | OVERFILLED
|  |  | LEGACY MINIMUM | UHS IT STANDARD
HIGH | MEP | LIGHTS | SUFFICIENT | EMERGENCY | EMERGENCY | HOUSE POWER | UNKNOWN SUFFICIENT | NOT SUFFICIENT
HIGH |  | HVAC | DEDICATED | DEDICATED | DEDICATED | BUILDING AIR | NONE | UNKNOWN
|  | HVAC TYPE | ANY | ANY | CHILLED WATER | DX | BOTH | UNKNOWN
MED |  | WALL POWER | EMERGENCY OR HOUSE | EMERGENCY, IF AVAILABLE | EMERGENCY | HOUSE POWER | NONE | UNKNOWN
HIGH |  | RACK POWER -TWIST LOCK | EMERGENCY OR HOUSE | EMERGENCY, IF AVAILABLE | EMERGENCY | HOUSE POWER | NONE
HIGH |  | RACK POWER - NON LOCKING | EMERGENCY OR HOUSE | EMERGENCY, IF AVAILABLE | EMERGENCY | HOUSE POWER | NONE
MED |  | POSITIVE PRESSURE | YES | YES | YES | NO
|  |  | LEGACY MINIMUM | UHS IT STANDARD
HIGH | GROUNDING AND BONDING | 12" X 4" TMGB OR SBB | YES | YES | YES | NO | UNDERSIZED
HIGH |  | TWO HOLE TUGS USED | YES | YES | YES | NO
HIGH |  | TRAY BONDED TO TGB | YES | YES | YES | NO
HIGH |  | RACK BONDED TO TGB | YES | YES | YES | NO
HIGH |  | UPS BONDED TO RACK | YES | YES | YES | NO
HIGH |  | PDU(S) BONDED TO RACK | YES OR NA | YES | YES | NO | NA
HIGH |  | OSP CABLE EQUIPMENT | YES OR NA | YES OR NA | YES | NO | NA
|  |  | LEGACY MINIMUM | UHS IT STANDARD
| RACK RELATED | NUMBER OF RACKS / CABINETS | SPARE RACK UNITS REQUIRED | 3 OR MORE | 1 | 2 | 3 | 4
MED |  | RACK 1 SPARE RACK UNITS | 5 RU OR MORE | 5 RU OR MORE | #
MED |  | RACK 2 SPARE RACK UNITS |  |  | #
MED |  | RACK 3 SPARE RACK UNITS |  |  | #
MED |  | RACK 4 SPARE RACK UNITS |  |  | #
MED |  | SPARE PATCH PANEL PORTS | 6 OR MORE | 6 OR MORE | # | #
LOW |  | VERTICAL MANAGERS | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | REDRESSING REQUIRED | FULL | NONE
LOW |  | HORIZONTAL MANAGERS | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | REDRESSING REQUIRED | FULL | NONE
HIGH |  | FRONT CLEARANCE | 3FT+ | 3FT+ | 3FT+ | 2FT+ | NONE | UNSAFE
HIGH |  | REAR CLEARANCE | 3FT+ | 3FT+ | 3FT+ | 2FT+ | NONE | UNSAFE
LOW |  | ROOM FOR ADDITIONAL RACK | YES OR EMPTY RACKS AVAILABLE | YES OR EMPTY RACKS AVAILABLE | YES | NO, EMPTY RACK(S) AVAILABLE | NONE
|  |  | LEGACY MINIMUM | UHS IT STANDARD
| UPS | UPS SIZE | N/A | N/A | 1500W | 5000W | 3000W | NONE
HIGH |  | UPS STATUS | PASSED TEST | PASSED TEST | PASSED TEST | FAILS TEST | NONE
MED |  | UPS MONITORED | YES | YES | YES | NO
MED |  | ROOM TEMP MONITORING | YES | YES | YES | NO
|  | STEP DOWN TRANSFORMER | ANY | ANY | YES | NO | NA
|  |  | LEGACY MINIMUM | UHS IT STANDARD
LOW | LABELING | ROOM | YES | YES | YES | NO
LOW |  | RACKS | YES | YES | YES | NO
LOW |  | FIBER CABLE | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | FIBER PANEL | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | BACKBONE COPPER CABLE | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | BACKBONE COPPER PANEL | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | HORIZONTAL CABLE | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | HORIZONTAL PATCH PANEL | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | SWITCHES | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | UPS | YES | YES | YES | NO | UPDATE REQUIRED
HIGH |  | BUSS BAR | YES | YES | YES | NO | UPDATE REQUIRED
HIGH |  | FIRE STOP ASSEMBLIES | YES | YES | YES | NO | UPDATE REQUIRED
|  |  | LEGACY MINIMUM | UHS IT STANDARD
| BACKBONE | FIBER CABLE MFG | BUILDING SPECIFIC | BUILDING SPECIFIC | COMMSCOPE | CORNING | PYRSMIAN | DRAKA
|  | FIBER CONNECTIVITY | ANY | LC | LC | ST | APC | SC
MED |  | FIBER AT CAPACITY | NO | NO | YES | NO
|  | BACKBONE COPPER CABLE | ANY | BUILDING SPECIFIC | 25 PAIR | 50 PAIR | 100 PAIR | NONE
MED |  | COPPER BACKBONE AT CAPACITY | NO | NO | YES | NO
|  |  | LEGACY MINIMUM | UHS IT STANDARD
| HORIZ. COPPER | HORIZONTAL CABLE MFG |  |  | COMMSCOPE | PANDUIT / GENERAL | BERKTEK | ICC | OTHER
|  | HORIZONTAL CONNECTIVITY | BUILDING SPECIFIC | BUILDING SPECIFIC | COMMSCOPE | PANDUIT | LEVITON | ICC | OTHER
MED |  | CATEGORY | CATEGORY 6 OR BETTER | CATEGORY 6 OR BETTER | CATEGORY 3 | CATEGORY 5 / 5E | CATEGORY 6/6E | CATEGORY 6A | COMBINATION
MED |  | SPARE PORTS ON PANEL | 6 OR MORE | 6 OR MORE | #
|  |  | LEGACY MINIMUM | UHS IT STANDARD
| COAX | RISER | ANY | NONE | 0.500 HARDLINE | RG-59 | RG-6 | NONE
LOW |  | HORIZONTAL COAX | ANY | NO | YES | NO |  | NONE

## Interior Enclosure
INTERIOR ENCLOSURES - WALL OR FLOOR-MOUNTED ENCLOSURES OR CABINETS WITH VENTILATION OR ACTIVE COOLING.
|  |  | LEGACY MINIMUM | UHS IT STANDARD
| GENERAL | DATE / TIME |  |  | DATE AND TIME
|  | INSPECTOR NAME |  |  | #
|  | CAMPUS |  |  | CLEAR LAKE | DOWNTOWN | MAIN | VICTORIA
|  | BUILDING |  |  | TEXT
|  | ROOM TYPE | LEGACY OR LEGACY CIR | STANDARD OR STANDARD CIR | STANDARD | LEGACY | STANDARD CIR | STANDARD CIR
|  | ROOM NUMBER |  |  | TEXT
HIGH |  | TEMPERATURE | 60 - 75F | 60 - 75F | #
HIGH |  | HUMIDITY | 30 - 50% RH | 30 - 50% RH | #
HIGH |  | ASSET TAG ON DOOR FRAME | YES | YES | # | NONE
HIGH |  | ENCLOSURE ID | YES | YES | YES | NOT CONTROLLABLE | NONE IN ROOM
|  |  | LEGACY MINIMUM | UHS IT STANDARD
HIGH | ROOM INFORMATION | ROOM OWNER | ANY | ANY | IT | SHARED | OTHERS
HIGH |  | SPACE USE | ANY | ANY | DEDICATED (IT) | APPROVED MULTI-USE | UTILITY / MECHANICAL | OTHER
HIGH |  | ACCESS | ANY, BUT OTHER | ANY, BUT OTHER | READER W/ IT MASTER KEY | IT MASTER KEYED | COMMON KEYED (ENCLOSURE SECURED) | NONE (ENCLOSURE SECURED) | OTHER
|  | CLEARANCE | SAFE TO ACCESS | 3FT+ | 3FT+ | SAFE TO ACCESS | NOT SAFE TO ACCESS
HIGH |  | LIGHTING | OPERATIONAL | OPERATIONAL | SWITCH | MOTION | NONE | SWITCH NON OPERATIONAL | MOTION NON OPERATIONAL
HIGH |  | WALLS TO DECK | YES OR NO (ENCLOSURE SECURED) | YES OR NO (ENCLOSURE SECURED) | YES | NO (ENCLOSURE SECURED) | NO
HIGH |  | POWER CORD TRIPPING HAZARD | NO | NO | NO | YES
|  | CAMERA (INTERIOR TO ROOM) | YES | YES | YES | NO
|  |  | LEGACY MINIMUM | UHS IT STANDARD
LOW | HOUSE KEEPING | TRASH IN ENCLOSURE | NO | NO | NO | YES, REMOVE
LOW |  | ENCLOSURE EXTERIOR IS CLEAN | YES | YES | YES | NO, CLEANING REQUIRED
LOW |  | EQUIPMENT DUST FREE | YES | YES | YES | NO , CLEANING REQUIRED
MED |  | INAPROPRIATE STORAGE | NO | NO | NO | YES
HIGH |  | ABANDONED CABLING | NO | NO | NO | YES
|  |  | LEGACY MINIMUM | UHS IT STANDARD
HIGH | NON SERVICING SYSTEMS | WATER PIPES ABOVE | NO OR DRIP PAN INSTALLED | NO | NO | YES, DRIP PAN INSTALLED | YES, DRIP PAN NEEDED
HIGH |  | SEWER PIPES ABOVE | NO OR DRIP PAN INSTALLED | NO | NO | YES, DRIP PAN INSTALLED | YES, DRIP PAN NEEDED
HIGH |  | FIRE MAIN ABOVE | NO OR DRIP PAN INSTALLED | NO | NO | YES, DRIP PAN INSTALLED | YES, DRIP PAN NEEDED
HIGH |  | ROOF DRAINS ABOVE | NO OR DRIP PAN INSTALLED | NO | NO | YES, DRIP PAN INSTALLED | YES, DRIP PAN NEEDED
|  |  | LEGACY MINIMUM | UHS IT STANDARD
MED | CABLE SUPPORT | INCOMING CABLE SUPPORT | ANY (NOT NONE) | ANY (NOT NONE) | BASKET/LADDER | CONDUIT | HOOKS | NONE, SUPPORT REQUIRED
MED |  | WALL CABLE SUPPORT | ANY (NOT NONE) | LADDER | BASKET/LADDER | CONDUIT | D-RINGS | NONE, SUPPORT REQUIRED
MED |  | SUPPORT CAPACITY | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | SUPPORT FULL | REWORK REQUIRED
LOW |  | CABLE TRAY DRESSING | NEAT AND TIDY | NEAT AND TIDY | NEAT AND TIDY | REDRESSING REQUIRED
HIGH |  | HORIZONTAL PENETRATIONS | COMPLIANT OR SEALED | FIRE-STOP COMPLIANT | FIRE-STOP COMPLIANT | FIRE-STOP NON COMPLIANT | PENETRATIONS SEALED | PENETRATIONS NOT SEALED
MED |  | HORZ. PENETRATION SPACE | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | FULL | OVERFILLED
HIGH |  | VERTICAL PENETRATIONS | FIRE-STOP COMPLIANT | FIRE-STOP COMPLIANT | FIRE-STOP COMPLIANT | FIRE-STOP NON COMPLIANT | NOT APPLICABLE
MED |  | VERTL PENETRATION SPACE | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | FULL | OVERFILLED
HIGH |  | INCOMMING OSP CONDUIT | FIRE-STOP COMPLIANT | FIRE-STOP COMPLIANT | FIRE-STOP COMPLIANT | FIRE-STOP NON COMPLIANT | PENETRATIONS SEALED | PENETRATIONS NOT SEALED
MED |  | OSP CONDUIT SPACE | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | FULL | OVERFILLED
|  |  | LEGACY MINIMUM | UHS IT STANDARD
HIGH | MEP | LIGHTS | SUFFICIENT | SUFFICIENT | EMERGENCY | HOUSE POWER | UNKNOWN SUFFICIENT | NOT SUFFICIENT
HIGH |  | HVAC | DEDICATED OR BUILDING | DEDICATED OR BUILDING | DEDICATED | BUILDING AIR | NONE | UNKNOWN
|  | HVAC TYPE | ANY | ANY | CHILLED WATER | DX | BOTH | UNKNOWN
MED |  | ENCLOSURE POWER | EMERGENCY OR HOUSE | EMERGENCY, IF AVAILABLE | EMERGENCY | HOUSE POWER | NONE | UNKNOWN
HIGH |  | PLUG FOR ENCLOSURE | TWISTLOCK OR INTERNAL | TWISTLOCK OR INTERNAL | TWISTLOCK | INTERNAL TO ENCLOSURE | NON-LOCKING OUTSIDE OF ENCLOSURE | HARDWIRED
HIGH |  | ENCLOSURE COOLING | EMERGENCY OR HOUSE | EMERGENCY, IF AVAILABLE | ACTIVE | VENTILATED | NONE
|  |  | LEGACY MINIMUM | UHS IT STANDARD
HIGH | GROUNDING AND BONDING | ENCLOSURE BONDING | ANY, BUT NONE | TO TGB OR SBB | TO TGB OR SBB | TO BUILDING STEEL | TO ELECTRICAL GROUND | NONE
HIGH |  | TWO HOLE TUGS USED | YES | YES | YES | NO
HIGH |  | TRAY BONDED TO TGB | YES | YES | YES | NO
HIGH |  | RACK BONDED TO TGB | YES | YES | YES | NO
HIGH |  | UPS BONDED TO RACK | YES | YES | YES | NO
HIGH |  | PDU(S) BONDED TO RACK | YES OR NA | YES | YES | NO | NA
|  |  | LEGACY MINIMUM | UHS IT STANDARD
| ENCLOSURE INFO | ENCLOSURE TYPE |  |  | WALL-MOUNTED CABINET | FLOOR-MOUNTED CABINET | NEMA ENCLOSURE | OTHER
MED |  | SPARE CAPACITY | YES | YES | YES | NO
MED |  | NETWORK EQUIPMENT TYPE | ANY | ANY | NETWORK SWITCH | HARDENED SWITCH | POWERED FIBER | MEDIA CONVERTER
MED |  | ENCLOSURE SECURITY | 1 OR MORE | 1 OR MORE | CARD READER | IT MASTER KEY | PAD LOCK WITH IT MASTER KEY | NONE
LOW |  | VERTICAL MANAGERS | SPARE CAPACITY OR N/A | SPARE CAPACITY OR N/A | SPARE CAPACITY | REDRESSING REQUIRED | FULL | N/A
LOW |  | HORIZONTAL MANAGERS | SPARE CAPACITY OR N/A | SPARE CAPACITY OR N/A | SPARE CAPACITY | REDRESSING REQUIRED | FULL | N/A
HIGH |  | FRONT CLEARANCE | 3FT+ | 3FT+ | 3FT+ | 2FT+ | NONE | UNSAFE
HIGH |  | REAR CLEARANCE | 3FT+ OR N/A | 3FT+ OR N/A | 3FT+ | 2FT+ | N/A | UNSAFE
|  |  | LEGACY MINIMUM | UHS IT STANDARD
| UPS | UPS SIZE | ANY | ANY | 1500W | 5000W | 3000W | NONE
HIGH |  | UPS STATUS | PASSED TEST | PASSED TEST | PASSED TEST | FAILS TEST | NONE
MED |  | UPS MONITORED | YES OR N/A | YES OR N/A | YES | NO | N/A
MED |  | ROOM TEMP MONITORING | YES | YES | YES | NO
|  | STEP DOWN TRANSFORMER | ANY | ANY | YES | NO | NA
|  |  | LEGACY MINIMUM | UHS IT STANDARD
LOW | LABELING | ROOM | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | ENCLOSURE | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | FIBER CABLE | YES | YES | YES | NO | UPDATE REQUIRED | N/A
LOW |  | FIBER PANEL | YES | YES | YES | NO | UPDATE REQUIRED | N/A
LOW |  | BACKBONE COPPER CABLE | YES | YES | YES | NO | UPDATE REQUIRED | N/A
LOW |  | BACKBONE COPPER PANEL | YES | YES | YES | NO | UPDATE REQUIRED | N/A
LOW |  | HORIZONTAL CABLE | YES | YES | YES | NO | UPDATE REQUIRED | N/A
LOW |  | HORIZONTAL PATCH PANEL | YES | YES | YES | NO | UPDATE REQUIRED | N/A
LOW |  | SWITCHES | YES | YES | YES | NO | UPDATE REQUIRED | N/A
LOW |  | UPS | YES | YES | YES | NO | UPDATE REQUIRED | N/A
HIGH |  | BUSS BAR | YES | YES | YES | NO | UPDATE REQUIRED | N/A
HIGH |  | FIRE STOP ASSEMBLIES | YES | YES | YES | NO | UPDATE REQUIRED | N/A
|  |  | LEGACY MINIMUM | UHS IT STANDARD
| BACKBONE | FIBER CABLE MFG | ANY | ANY | COMMSCOPE | CORNING | PYRSMIAN | DRAKA
|  | FIBER CONNECTIVITY | ANY | LC | LC | ST | APC | SC
MED |  | FIBER AT CAPACITY | NO | NO | YES | NO
|  | BACKBONE COPPER CABLE | ANY | ANY | 25 PAIR | 50 PAIR | 100 PAIR | NONE
MED |  | COPPER BACKBONE AT CAPACITY | NO | NO | YES | NO
|  |  | LEGACY MINIMUM | UHS IT STANDARD
| HORIZ. COPPER | HORIZONTAL CABLE MFG |  |  | COMMSCOPE | PANDUIT / GENERAL | BERKTEK | ICC | OTHER
|  | HORIZONTAL CONNECTIVITY | ANY | ANY | COMMSCOPE | PANDUIT | LEVITON | ICC | OTHER
MED |  | CATEGORY | CATEGORY 6 OR BETTER | CATEGORY 6 OR BETTER | CATEGORY 3 | CATEGORY 5 / 5E | CATEGORY 6/6E | CATEGORY 6A | COMBINATION
MED |  | SPARE PORTS ON PANEL | 6 OR MORE | 6 OR MORE | #
|  |  | LEGACY MINIMUM | UHS IT STANDARD
| COAX | RISER | ANY | NONE | 0.500 HARDLINE | RG-59 | RG-6 | NONE
LOW |  | HORIZONTAL COAX | ANY | NO | YES | NO |  | NONE

## Exterior Enclosure
EXTERIOR ENCLOSURES - WALL , SLAB OR POLE MOUNTED ENCLOSURES OR CABINETS WITH ACTIVE COOLING OR HARDENED EQUIPMENT.
|  |  | LEGACY MINIMUM | UHS IT STANDARD
| GENERAL | DATE / TIME |  |  | DATE AND TIME
|  | INSPECTOR NAME |  |  | #
|  | CAMPUS |  |  | CLEAR LAKE | DOWNTOWN | MAIN | VICTORIA
|  | CLOSEST BUILDING |  |  | TEXT
|  | GIS LOCATION |  |  | TEXT
|  | ENCLOSURE MOUNTING | ANY | ANY | WALL | SLAB | POLE | OTHER
HIGH |  | INTERIOR TEMPERATURE | 60 - 75F OR HARDENED EQUIPMENT | 60 - 75F OR HARDENED EQUIPMENT | #
HIGH |  | EQUIPMENT TYPE | STANDARD OR HARDENED | STANDARD OR HARDENED | STANDARD | HARDENED
HIGH |  | ENCLOSURE MATERIAL | STAINLESS OR ALUMINIUM | STAINLESS OR ALUMINIUM | STAINLESS | ALUMINIUM | GALVANIZED | OTHER
HIGH |  | ENCLOSURE ID | TEXT | TEXT | TEXT | NONE | NOT LEGIBLE
|  |  | LEGACY MINIMUM | UHS IT STANDARD
LOW | HOUSE KEEPING | TRASH IN ENCLOSURE | NO | NO | NO | YES, REMOVE
LOW |  | ENCLOSURE EXTERIOR IS CLEAN | YES | YES | YES | NO, CLEANING REQUIRED
LOW |  | EQUIPMENT DUST FREE | YES | YES | YES | NO , CLEANING REQUIRED
MED |  | ENCLOSURE CONDITION | ACCEPTABLE | ACCEPTABLE | ACCEPTABLE | DENTED / RUSTED, ETC
HIGH |  | ABANDONED CABLING | NO | NO | NO | YES
|  |  | LEGACY MINIMUM | UHS IT STANDARD
HIGH | NON SERVICING SYSTEMS | WATER PIPES ABOVE | NO OR DRIP PAN INSTALLED | NO | NO | YES, DRIP PAN INSTALLED | YES, DRIP PAN NEEDED
HIGH |  | SEWER PIPES ABOVE | NO OR DRIP PAN INSTALLED | NO | NO | YES, DRIP PAN INSTALLED | YES, DRIP PAN NEEDED
HIGH |  | FIRE MAIN ABOVE | NO OR DRIP PAN INSTALLED | NO | NO | YES, DRIP PAN INSTALLED | YES, DRIP PAN NEEDED
HIGH |  | ROOF DRAINS ABOVE | NO OR DRIP PAN INSTALLED | NO | NO | YES, DRIP PAN INSTALLED | YES, DRIP PAN NEEDED
|  |  | LEGACY MINIMUM | UHS IT STANDARD
MED | CABLE SUPPORT | INCOMING CABLE SUPPORT | ANY (NOT NONE) | ANY (NOT NONE) | N/A | CONDUIT | HOOKS | NONE, SUPPORT REQUIRED
MED |  | WALL CABLE SUPPORT | ANY (NOT NONE) | LADDER | N/A | CONDUIT | D-RINGS | NONE, SUPPORT REQUIRED
MED |  | SUPPORT CAPACITY | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | SUPPORT FULL | REWORK REQUIRED
LOW |  | CABLE TRAY DRESSING | NEAT AND TIDY | NEAT AND TIDY | NEAT AND TIDY | REDRESSING REQUIRED
HIGH |  | HORIZONTAL PENETRATIONS | COMPLIANT OR SEALED | FIRE-STOP COMPLIANT | FIRE-STOP COMPLIANT | FIRE-STOP NON COMPLIANT | PENETRATIONS SEALED | PENETRATIONS NOT SEALED
MED |  | HORZ. PENETRATION SPACE | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | FULL | OVERFILLED
HIGH |  | VERTICAL PENETRATIONS | FIRE-STOP COMPLIANT | FIRE-STOP COMPLIANT | FIRE-STOP COMPLIANT | FIRE-STOP NON COMPLIANT | NOT APPLICABLE
MED |  | VERTL PENETRATION SPACE | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | FULL | OVERFILLED
HIGH |  | INCOMMING OSP CONDUIT | FIRE-STOP COMPLIANT | FIRE-STOP COMPLIANT | FIRE-STOP COMPLIANT | FIRE-STOP NON COMPLIANT | PENETRATIONS SEALED | PENETRATIONS NOT SEALED
MED |  | OSP CONDUIT SPACE | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | FULL | OVERFILLED
|  |  | LEGACY MINIMUM | UHS IT STANDARD
HIGH | MEP | LIGHTS | SUFFICIENT | SUFFICIENT | EMERGENCY | HOUSE POWER | UNKNOWN SUFFICIENT | NOT SUFFICIENT
MED |  | ENCLOSURE POWER | EMERGENCY OR HOUSE | EMERGENCY, IF AVAILABLE | EMERGENCY | HOUSE POWER | POWERED FIBER | NONE
HIGH |  | PLUG FOR ENCLOSURE | INTERNAL | INTERNAL | SOLAR | INTERNAL TO ENCLOSURE | NON-LOCKING OUTSIDE OF ENCLOSURE | POWERED FIBER
HIGH |  | ENCLOSURE COOLING | ANY | ANY | ACTIVE | VENTILATED | NONE
|  |  | LEGACY MINIMUM | UHS IT STANDARD
HIGH | GROUNDING AND BONDING | ENCLOSURE BONDING | ANY, BUT NONE | ANY BUT NONE | TO GROUND ROD | TO BUILDING STEEL OR POLE GROUD | VIA CONDUIT W/BRAIDED BONDING JUMPER | NONE
HIGH |  | GROUNDING BAR IN ENCLOSURE | YES OR NA | YES OR NA | YES | NO | NA
HIGH |  | LIGHTING ARRESTORS USED | YES OR NA | YES OR NA | YES | NO | NA
HIGH |  | ARRESTORS BONDED PROPERLY | YES OR NA | YES OR NA | YES | NO | NA
HIGH |  | UPS BONDED TO RACK | YES OR NA | YES OR NA | YES | NO | NA
HIGH |  | PDU(S) BONDED TO RACK | YES OR NA | YES OR NA | YES | NO | NA
|  |  | LEGACY MINIMUM | UHS IT STANDARD
| ENCLOSURE INFO | ENCLOSURE TYPE |  |  | AIR CONDITIONED EXTERIOR CABINET | NEMA 4X ENCLOSURE | STANDARD PULL BOX | OTHER
MED |  | SPARE CAPACITY | YES | YES | YES | NO
MED |  | NETWORK EQUIPMENT TYPE | ANY | ANY | NETWORK SWITCH | HARDENED SWITCH | POWERED FIBER | MEDIA CONVERTER/EXTENDER
MED |  | ENCLOSURE SECURITY | 1 OR MORE | PAD LOCK WITH IT MASTER KEY | PAD LOCK WITH IT MASTER KEY | IT MASTER KEY | SECURITY SCREWS | NONE
LOW |  | VERTICAL MANAGERS | SPARE CAPACITY OR N/A | SPARE CAPACITY OR N/A | SPARE CAPACITY | REDRESSING REQUIRED | FULL | N/A
LOW |  | HORIZONTAL MANAGERS | SPARE CAPACITY OR N/A | SPARE CAPACITY OR N/A | SPARE CAPACITY | REDRESSING REQUIRED | FULL | N/A
HIGH |  | FRONT CLEARANCE | 3FT+ | 3FT+ | 3FT+ | 2FT+ | NONE | UNSAFE
HIGH |  | REAR CLEARANCE | 3FT+ OR N/A | 3FT+ OR N/A | 3FT+ | 2FT+ | N/A | UNSAFE
|  |  | LEGACY MINIMUM | UHS IT STANDARD
| UPS | UPS SIZE | ANY | ANY | 1500W | 5000W | 3000W | NONE
HIGH |  | UPS STATUS | PASSED TEST OR N/A | PASSED TEST OR N/A | PASSED TEST | FAILS TEST | NONE | N/A
MED |  | UPS MONITORED | YES OR N/A | YES OR N/A | YES | NO | N/A
MED |  | ROOM TEMP MONITORING | YES OR N/A | YES | YES | NO | N/A
|  | STEP DOWN TRANSFORMER | ANY | ANY | YES | NO | N/A
|  |  | LEGACY MINIMUM | UHS IT STANDARD
LOW | LABELING | POLE | YES OR N/A | YES OR N/A | YES | NO | UPDATE REQUIRED | N/A
LOW |  | ENCLOSURE | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | FIBER CABLE | YES OR N/A | YES OR N/A | YES | NO | UPDATE REQUIRED | N/A
LOW |  | FIBER PANEL | YES OR N/A | YES OR N/A | YES | NO | UPDATE REQUIRED | N/A
LOW |  | BACKBONE COPPER CABLE | YES OR N/A | YES OR N/A | YES | NO | UPDATE REQUIRED | N/A
LOW |  | BACKBONE COPPER PANEL | YES OR N/A | YES OR N/A | YES | NO | UPDATE REQUIRED | N/A
LOW |  | HORIZONTAL CABLE | YES OR N/A | YES OR N/A | YES | NO | UPDATE REQUIRED | N/A
LOW |  | HORIZONTAL PATCH PANEL | YES OR N/A | YES OR N/A | YES | NO | UPDATE REQUIRED | N/A
LOW |  | SWITCHES | YES OR N/A | YES OR N/A | YES | NO | UPDATE REQUIRED | N/A
LOW |  | UPS | YES OR N/A | YES OR N/A | YES | NO | UPDATE REQUIRED | N/A
HIGH |  | BUSS BAR | YES OR N/A | YES OR N/A | YES | NO | UPDATE REQUIRED | N/A
HIGH |  | FIRE STOP ASSEMBLIES | YES OR N/A | YES OR N/A | YES | NO | UPDATE REQUIRED | N/A
|  |  | LEGACY MINIMUM | UHS IT STANDARD
| BACKBONE | FIBER CABLE MFG | ANY | ANY | COMMSCOPE | CORNING | PYRSMIAN | DRAKA
|  | FIBER CONNECTIVITY | ANY | LC | LC | ST | APC | SC
MED |  | FIBER AT CAPACITY | NO | NO | YES | NO
|  | BACKBONE COPPER CABLE | ANY | ANY | 25 PAIR | 50 PAIR | 100 PAIR | NONE
MED |  | COPPER BACKBONE AT CAPACITY | NO | NO | YES | NO
|  | WIRELESS |  |  | POINT TO POINT | BRIDGE | N/A
|  | POWERED FIBER |  |  | YES | NO
|  |  | LEGACY MINIMUM | UHS IT STANDARD
| HORIZ. COPPER | HORIZONTAL CABLE MFG |  |  | COMMSCOPE | PANDUIT / GENERAL | BERKTEK | ICC | OTHER
|  | HORIZONTAL CONNECTIVITY | ANY | ANY | COMMSCOPE | PANDUIT | LEVITON | ICC | OTHER
MED |  | CATEGORY | CATEGORY 6 OR BETTER | CATEGORY 6 OR BETTER | CATEGORY 3 | CATEGORY 5 / 5E | CATEGORY 6/6E | CATEGORY 6A | COMBINATION
MED |  | CABLE TYPE | OSP | OSP | OSP RATED | PVC | PLENUM
|  |  | LEGACY MINIMUM | UHS IT STANDARD
| COAX | RISER | ANY | NONE | 0.500 HARDLINE | RG-59 | RG-6 | NONE
LOW |  | HORIZONTAL COAX | ANY | NO | YES | NO |  | NONE